HOW TO CALCULATE VOLTAGE LOSSES ON A RUN OF COPPER CABLE
by Chris Meagher VK2ACD

Use this simple formula

V = I x L x 0.019
   A
V = Voltage drop, in volts
I = Current in ampere
L = Cable length, in metres
A = Cross-sectional area of cable, in square mm

The formula can be transposed, to determine the cable size
required for a pre-determined acceptable voltage drop:

A = I x L x 0.019
  V

Example:

You have a solar panel array that can generate 30 amps maximum.
You can accept a voltage drop from panels to regulator of 1 volt,
over a distance of 10 metres.

First, note that the cable length will be 20 metres, since the current has to
travel both ways.

Therefore,

A = 30 (amps) x 20 (metres) x 0.019 = 11.4 square mm
1 (volt)

How much power is lost?

Use the equation P = V x I
Power loss is then 1 (volt) x 30 (amps) = 30 Watts.
This is consumed by heating the cable.

Where does the value of 0.019 come from?

The resistance of a copper cable, of cross-section area 1 square mm,
is about 0.019 per metre.